## Slide 1: Surface Cable Assembly (SCA)

## Slide 2: Purpose
(photo of west tower)
Pass electrical signals from the down hole main cable to the IceCube Lab
Runs from ICL to Surface Junction Box
One cable for each Upgrade String (7)

## Slide 3: Cable Entry
surface cables x7
culvert
removable panel
(photo of west tower)

## Slide 4: Length Planning: Trench Routes

## Slide 5: Length Planning: Tower & Bridge Run
4.6
9.0
0.9
8.4
[m]
slack loop = 2*4.6m
tower elevation and bridge = 9 + 0.9 + 8.4m
xy routing: 2.5m
2.5

## Slide 6: Length Planning: Server Room Routing
Distance to patch panel [m]
  x ≤ 7.7
  y ≤ 1.1
  z ≤ 2.5
7.7
1.1
2.5
Cable shield connection
at ICL server room entry
(mid-span strip when installed)
4.3
3.4

## Slide 7: Contingency: Trench Rerouting
+13m
+7m
+6m
+15m covers reasonable trench rerouting

## Slide 8: Surface Cable Length
Segment | Length (m)
central SJB to cable tower center (XY) | 62 / 66
central SJB to cable tower base (Z) | 2
cable tower slack loop (30 years) | 10
cable tower rise + cable bridge | 21
contingency: trench move | 15
contingency: tower / ICL rerouting | 5
quad length: ICL entry to patch panel (max) | 12 (2.5 unsheathed)
quad length: SJB entry to patch panel (max) | 3 (unsheathed)
cable length (connector to connector, max) | 134
NB: by using longest trench route, we avoid issues with moving a string from one trench to the another (2+5 deployment scenario)

## Slide 9: SURFACE CABLE DRAWING
Prototype photo

## Slide 10: SJB patch panel / quad lengths

## Slide 11: ICL patch panel / quad lengths
Quad connector lengths staggered based on patch panel layout; optimization TBD (min 177”-15”; max 177")
FRONT
dimensions in inches

## Slide 12: Datasheet

## Slide 14: Surface cable spools delivered